## Consolidated
Category | Scope | Accounted in BCA Report | Price ex gst | Comments
Common Area | Replace missing barrier at level 2 staircase | Yes
Common Area | Internal Paint | No
Common Area | Line Marking/rear concreting only like for like | No
Common Area | Fencing at Rear | No
Common Area | Scaffolding | No
Common Area | Roof Report Provided | No
Common Area | Switch Board Upgrade | No
Common Area | Replace door hardware - excluding door closer (2x entry/exit) | Yes
Total
Units | Replace door hardware - excluding door closer (2x entry/exit) | Yes
Units | Replace SOU balcony balustrades (~148m total) x 12 | No
Units | Window restrictors to 125 mm opening (12 units) | No
Units | Bathroom Replacement x 12 | No
Units | Kitchen Replacement x 12 | No
Units | Vinyl Replacement (Lounge, Hall, Bed 1 & Bed 2) x 12 | No
Units | Full Internal Paint x 12 | No
Units | Light Replacement | No
Units | Renew Taps in Laundry | No
Units | Fuse box upgrades | No
Units | Remove AC units x 12 | No
u nits | Balcony tiling x 12 | No
Total
As per Report Provided
Fire Safety | Renew single fire door and frame and hardware (-/120/30) | Yes
Fire Safety | Test and Certify SOU door frames (tags) | No
Fire Safety | Hilti CP636 firestop mortar – firestop openings | No
Fire Safety | Hilti CP601S elastic fire stop sealant (310ml) | No
Fire Safety | New Fire Hose Reels – supply & install 3 x FHR | Yes
Fire Safety | Emergency lights – 6x in common areas (interconnected) | No
Fire Safety | Interconnect up to 5 smoke alarms – common areas | No
Fire Safety | Replace photoelectric type smoke alarms (common areas?) | Yes
Fire Safety | Illuminated exit sign(s) | No
Fire Safety | Interconnect group of 6–10 smoke alarms – common areas | No
Fire Safety | AS2293 test switch on separate circuit (emergency/exit) | No
Fire Safety | New fire rated ceiling/cornice in top-floor 2BD SOUs | Yes
Fire Safety | Bulkheads for PVC penetrations (x4) | Yes
Fire Safety | Replace with (-/60/30) door frame up to 2.1 m | Yes
Fire Safety | Tenmat FF109 downlight covers – 150 mm dia | Yes
Total
Total Ex gst

## BCA_Extract
BCA Report (actionable)
d3d21 wire barriers n/a
windows non-compliant all the sou s the window latches are not fitted and don t
limit the window opening to less than 125 mm
e1d3 fire hose reels non-compliant hose reels are not installed
1 the inspection noticed that the pvc penetration in the garages are not sealed properly all
the pvc penetrations are required to be properly sealed fire collars and copper penetration
underside of the non-combustible roof suggest to upgrade the ceiling to fire rated for the
top floor units to be confirmed by the contractors on site if the ceiling is fire rated
3 inspection found that old smoke alarm installed in the common staircase however these
smoke alarms are not interconnected smoke alarm has exceeded its service life and requires
4 all the sous smoke alarms have exceeded the service life and requires replacement we
recommended to replace the smoke alarms with hard wired 240 v smoke alarms
5 all sou entrance doors were identified as fire doors but the door frames are missing the tag
6 sous don t have window latches or restrictors to limit the window opening to less than 125
mm bca 2022 ncc 2022 stipulates that openable window sash must be restricted so that a
7 balcony balustrades are 1m in height replacement/upgrade of balustrades is required to
8 the inspection identified that illuminated exit signage and emergency lighting are not
provided within the property provide and install compliant illuminated exit signage and
emergency lighting to ensure occupants can safely and easily navigate the building during an
9 the inspection identified that fire hose reels are not provided at each level of the building
provide and install fire hose reels at every storey in accordance with ncc/bca requirements
renew single fire door and frame and
hardware -/120/30 install fire door for main switchboard
test and certify sou door frames test and certify the fire door frames
replace door hardware - excluding
firestop openings regrout the metal penetration openings
310ml cartridge seal all cable penetrations
bulkhead or ceiling including cutting
new fire hose reel supply and install 3 x fire hose reels
replace missing barrier at level 2
staircase replace missing barrier at level 2
replace the balustrades for the sou
balcony approx 148m 6 sou s and 8m each for 6 sou 12 sous with balustrade 20m e
be interconnected to the smoke
detection system in the building supply and install 6 x emergency lights
interconnection of a group of up to 5
smoke alarms in common areas interconnect common area smoke
alarm replace photoelectric type smoke alarm
illuminated exit sign illuminated exit sign
interconnection of a group of up to 6
to 10 smoke alarms in common areas interconnect exit signs and emergency
as2293 for emergency lighting and
as2293 for emergency lighting and exit
window winder restrictable to
restrict able window
new fire rated ceiling cornice for old -
in 2bd sou fire rated ceiling for top floor sou s to
be confirmed only if current ceiling is
bulkheads for pvc penetration supply and install bulkheads for vertical
pvc penetrations x 4
replace with -/60/30 door frame up
to 2 1m replace with -/60/30 door frame up to
tenmat ff109 downlight cover -
150mm dia downlight cover for all light fitting and
smoke alarms penetrating through fire
rated ceiling